## 31 Data Center
Uniformat | System | Componenet % of Total | Cost per S.F. | Cost | Floor Area (S.F.): | 16000
A1010 | Standard Foundations | 2.0411 | 8.1422 | 130275.9776 | Cost Per Square Foot: | 398.92
A1030 | Slab on Grade | 2.2267 | 8.8826 | 142121.6801 | Building Cost: | 6382757.45
B1010 | Floor Construction | 0.29511 | 1.1773 | 18836.066
B1020 | Roof Construction | 5.2815 | 21.069 | 337103.9282
B2010 | Exterior Walls | 4.1337 | 16.4903 | 263845.589
B2020 | Exterior Windows | 0.73316 | 2.9247 | 46795.9819
B2030 | Exterior Doors | 0.98312 | 3.9219 | 62750.1367
B3010 | Roof Coverings | 3.6848 | 14.6995 | 235192.2061
B3020 | Roof Openings | 0.25826 | 1.0302 | 16483.992
C1010 | Partitions | 2.4611 | 9.8178 | 157085.59
C1020 | Interior Doors | 1.2028 | 4.7981 | 76769.611
C1030 | Fittings | 0.10099 | 0.40288 | 6446.0278
C3010 | Wall Finishes | 1.327 | 5.2936 | 84697.2945
C3020 | Floor Finishes | 2.5978 | 10.3631 | 165809.5006
C3030 | Ceiling Finishes | 6.4516 | 25.737 | 411791.6402
D2010 | Plumbing Fixtures | 0.63916 | 2.5497 | 40795.7295
D2020 | Domestic Water Distribution | 0.2225 | 0.88762 | 14201.8693
D2040 | Rain Water Drainage | 0.11435 | 0.45616 | 7298.5904
D3010 | Energy Supply Systems | 2.2615 | 9.0215 | 144343.8896
D3020 | Heat Generating Systems | 9.4228 | 37.5896 | 601432.8733
D3030 | Cooling Generating Systems | 9.0459 | 36.086 | 577375.5584
D3040 | Distribution Systems | 13.9457 | 55.6325 | 890120.6525
D3060 | Controls & Instrumentation | 3.0153 | 12.0287 | 192458.5195
D4010 | Sprinklers | 1.8648 | 7.4389 | 119022.4799
D4020 | Standpipes | 0.33604 | 1.3405 | 21448.685
D5010 | Electrical Service/Distribution | 1.6325 | 6.5122 | 104195.3294
D5020 | Lighting and Branch Wiring | 6.1546 | 24.552 | 392832.2567
D5030 | Communications and Security | 11.0209 | 43.9648 | 703436.4044
D5090 | Other Electrical Systems | 3.9234 | 15.6513 | 250421.1818
F1020 | Integrated Construction | 2.6222 | 10.4604 | 167365.7353
Total |  | 100 | 398.9222 | 6382754.9768

## Squarefoot_Estimate
| Square Foot Cost Estimate Report |  |  | Date: | 6/17/2025
Estimate Name: | Data Center
Building Type: | Computer Data Center with E.I.F.S. / Rigid Steel
Location: | HELENA, MT
Story Count: | 1
Story Height (L.F.): | 16.50
Floor Area (S.F.): | 16000
Labor Type: | STD
Basement Included: | No | [5 empty] | Assembly Customization Type:
Data Release: | Year 2025 Quarter 2 | Costs are derived from a building model with basic components. | [5 empty] | Added
Cost Per Square Foot: | $398.92 | Scope differences and market conditions can cause costs to vary significantly. | [5 empty] | Partially Swapped
Building Cost: | $6,382,757.45 | [6 empty] | Fully Swapped
|  | Quantity | % of Total | Cost Per S.F. | Cost
A | Substructure |  | 4.27 | 12.73 | 203661.8 | 1
A1010 | Standard Foundations |  |  | 6.09 | 97402.6 | 3
A10101051560 | Foundation wall, CIP, 4' wall height, direct chute, .148 CY/LF, 7.2 PLF, 12" thick | 560 |  | 3.48 | 55754.16 | 4
A10101102700 | Strip footing, concrete, reinforced, load 11.1 KLF, soil bearing capacity 6 KSF, 12" deep x 24" wide | 672 |  | 2.24 | 35827.68 | 4
A10102107410 | Spread footings, 3000 PSI concrete, load 100K, soil bearing capacity 6 KSF, 4' - 6" square x 15" deep | 11.38 |  | 0.36 | 5820.76 | 4
A1030 | Slab on Grade |  |  | 6.64 | 106259.2 | 3
A10301202240 | Slab on grade, 4" thick, non industrial, reinforced | 16000 |  | 6.64 | 106259.2 | 4
B | Shell |  | 15.37 | 45.84 | 733463.85 | 1
B1010 | Floor Construction |  |  | 0.88 | 14083.04 | 3
B10107203700 | Fireproofing, gypsum board, fire rated, 2 layer, 1" thick, 14" steel column, 3 hour rating, 22 PLF | 296.8 |  | 0.88 | 14083.04 | 4
B1020 | Roof Construction |  |  | 15.75 | 252040.32 | 3
B10201245800 | Roof, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50' bay, 40 PSF superimposed load, 59" deep, 64 PSF total load | 16000 |  | 14.34 | 229421.6 | 4
B10201245850 | Roof, steel joists, joist girder, 1.5" 22 ga metal deck, on columns, 50'x50' bay, 40 PSF superimposed load, 59" deep, 64 PSF total load, add for columns | 16000 |  | 1.41 | 22618.72 | 4
B2010 | Exterior Walls |  |  | 12.33 | 197267.73 | 3
B20101525230 | E.I.F.S., cement board sheathing, 1x8 fascia, R8 insulation, 6" metal studs, 16" O.C., 2" EPS | 9044 |  | 12.33 | 197267.73 | 4
B2020 | Exterior Windows |  |  | 2.19 | 34987.65 | 3
B20201066850 | Windows, aluminum, sliding, insulated glass, 5' x 3' | 31.73 |  | 2.19 | 34987.65 | 4
B2030 | Exterior Doors |  |  | 2.93 | 46915.99 | 3
B20301106300 | Door, aluminum & glass, without transom, narrow stile, with panic hardware, 3'-0"x 7'-0"opening | 2.84 |  | 1.37 | 21946.6 | 4
B20301106950 | Door, aluminum & glass, with transom, narrow stile, double door, hardware, 6'-0" x 10'-0" opening | 1.42 |  | 1.56 | 24969.39 | 4
B3010 | Roof Coverings |  |  | 10.99 | 175844.64 | 3
B30101203400 | Roofing, single ply membrane, EPDM, 60 mils, loosely laid, stone ballast | 16000 |  | 2.46 | 39361.44 | 4
B30103202700 | Insulation, rigid, roof deck, extruded polystyrene, 40 PSI compressive strength, 4" thick, R20 | 16000 |  | 6.36 | 101787.84 | 4
B30104201500 | Roof edges, aluminum, duranodic, .050" thick, 8" face | 560 |  | 1.39 | 22272.18 | 4
B30106305400 | Gravel stop, aluminum, extruded, 8", duranodic, .050" thick | 560 |  | 0.78 | 12423.18 | 4
B3020 | Roof Openings |  |  | 0.77 | 12324.48 | 3
B30202100800 | Roof hatch, with curb, 1" fiberglass insulation, 2'x6" x 8'-0", aluminum curb and cover, 260 lbs | 1 |  | 0.23 | 3711.02 | 4
B30202102100 | Smoke hatch, unlabeled, galvanized, 2'-6" x 3', not incl hand winch operator | 2.84 |  | 0.54 | 8613.46 | 4
C | Interiors |  | 14.14 | 42.18 | 674840.87 | 1
C1010 | Partitions |  |  | 7.34 | 117447.17 | 3
C10101265425 | Metal partition, 5/8"fire rated gypsum board face, no base,3 -5/8" @ 24" OC framing, same opposite face, sound attenuation insulation | 14769.23 |  | 6.34 | 101451.77 | 4
C10101280700 | Gypsum board, 1 face only, exterior sheathing, fire resistant, 5/8" | 9044 |  | 0.67 | 10756.39 | 4
C10101280960 | Add for the following: taping and finishing | 9044 |  | 0.33 | 5239.01 | 4
C1020 | Interior Doors |  |  | 3.59 | 57397.84 | 3
C10201225220 | Wood door/metal frame, solid core/flush, oak face, 2'-8" x 6'-8", butt welded frame, 8-3/4" | 43.24 |  | 3.59 | 57397.84 | 4
C1030 | Fittings |  |  | 0.3 | 4819.46 | 3
C10301100560 | Toilet partitions, cubicles, floor and ceiling anchored, plastic laminate | 4.27 |  | 0.3 | 4819.46 | 4
C3010 | Wall Finishes |  |  | 3.96 | 63325.08 | 3
C30102300140 | Painting, interior on plaster and drywall, walls & ceilings, roller work, primer & 2 coats | 9044 |  | 0.53 | 8446.55 | 4
C30102300140 | Painting, interior on plaster and drywall, walls & ceilings, roller work, primer & 2 coats | 29538.46 |  | 1.72 | 27587.15 | 4
C30102301940 | Ceramic tile, thin set, 4-1/4" x 4-1/4" | 2953.85 |  | 1.71 | 27291.38 | 4
C3020 | Floor Finishes |  |  | 7.75 | 123969.72 | 3
C30204100080 | Carpet tile, nylon, fusion bonded, 18" x 18" or 24" x 24", 35 oz | 10400 |  | 3.86 | 61753.64 | 4
C30204101740 | Tile, porcelain type, minimum | 1600 |  | 1.49 | 23775.52 | 4
C30204101820 | Tile, quarry tile, mud set, maximum | 1600 |  | 2.4 | 38440.56 | 4
C3030 | Ceiling Finishes |  |  | 19.24 | 307881.6 | 3
C30302107400 | Acoustic ceilings, 3/4"mineral fiber, 12" x 12" tile, concealed 2" bar & channel grid, suspended support | 16000 |  | 19.24 | 307881.6 | 4
D | Services |  | 63.6 | 189.69 | 3035055.32 | 1
D2010 | Plumbing Fixtures |  |  | 1.91 | 30501.48 | 3
D20101102080 | Water closet, vitreous china, bowl only with flush valve, wall hung | 4.27 |  | 0.77 | 12278.19 | 4
D20102102000 | Urinal, vitreous china, wall hung | 1.42 |  | 0.16 | 2551.94 | 4
D20103102240 | Lavatory w/trim, wall hung, vitreous china, 24" x 20" | 2.84 |  | 0.25 | 3975.6 | 4
D20104101880 | Kitchen sink w/trim, countertop, stainless steel, 19" x 18" single bowl | 0.71 |  | 0.08 | 1281.21 | 4
D20104404260 | Service sink w/trim, PE on CI, corner floor, 28" x 28", w/rim guard | 0.71 |  | 0.23 | 3691.98 | 4
D20108202080 | Water cooler, electric, floor mounted, dual height, 14.3 GPH | 2.13 |  | 0.42 | 6722.56 | 4
D2020 | Domestic Water Distribution |  |  | 0.66 | 10618.22 | 3
D20202501860 | Gas fired water heater, commercial, 100< F rise, 100 MBH input, 91 GPH | 1.21 |  | 0.66 | 10618.22 | 4
D2040 | Rain Water Drainage |  |  | 0.34 | 5456.89 | 3
D20402102040 | Roof drain, DWV PVC, 4" diam, diam, 10' high | 2.84 |  | 0.29 | 4674.53 | 4
D20402102080 | Roof drain, DWV PVC, 4" diam, for each additional foot add | 18.49 |  | 0.05 | 782.36 | 4
D3010 | Energy Supply |  |  | 6.77 | 108258.56 | 3
D30105600400 | Hot water reheat system for 22,500 SF computer center | 16000 |  | 6.77 | 108258.56 | 4
D3020 | Heat Generating Systems |  |  | 12.33 | 197216.21 | 3
D30201061560 | Boiler, oil, cast iron, hot water, 236 MBH | 0.71 |  | 0.33 | 5246.08 | 4
D30203301020 | Pump, base mounted with motor, end-suction, 3" size, 5 HP, to 225 GPM | 4.27 |  | 6.8 | 108879.36 | 4
D30203301030 | Pump, base mounted with motor, end-suction, 4" size, 7-1/2 HP, to 350 GPM | 2.84 |  | 5.19 | 83090.77 | 4
D3030 | Cooling Generating Systems |  |  | 11.29 | 180679.82 | 3
D30301301030 | Chiller, reciprocating, water cooled, standard controls, 150 ton | 0.71 |  | 5.8 | 92757.33 | 4
D30303301030 | Cooling tower, stainless steel, packaged unit, draw thru, 300 ton | 0.71 |  | 5.5 | 87922.49 | 4
D3090 | Other HVAC Systems/Equip |  |  | 82.03 | 1312525.01 | 3
D30905100230 | Ductwork for 22,500 SF computer center | 16000 |  | 22.66 | 362516.8 | 4
D30905102090 | Plate heat exchanger, 400 GPM | 0.78 |  | 4.21 | 67423.64 | 4
D30909301020 | AHU, central station, cool/heat coils, VAV, filters, 10,000 CFM | 1.42 |  | 7.18 | 114811.73 | 4
D30909301040 | AHU, central station, cool/heat coils, VAV, filters, 20,000 CFM | 0.71 |  | 6.22 | 99448.18 | 4
D30909301050 | AHU, central station, cool/heat coils, VAV, filters, 30,000 CFM | 1.42 |  | 14.66 | 234635.38 | 4
D30909301060 | VAV terminal, cooling, hot water reheat, with actuator / controls, 1250 CFM | 19.91 |  | 21.3 | 340845.37 | 4
D30909301070 | VAV terminal, cool, hot water reheat, fan powered, with actuator/controls, 1250 CFM | 3.56 |  | 4.3 | 68845.69 | 4
D30909301080 | Roof vent. system, power, centrifugal, aluminum, galvanized curb, back draft damper, 800 CFM | 3.56 |  | 1.5 | 23998.22 | 4
D4010 | Sprinklers |  |  | 5.56 | 88988.77 | 3
D40103500580 | Preaction sprinkler systems, steel, black, sch 40, light hazard, 1 floor, 2000 SF | 2880 |  | 2.51 | 40165.86 | 4
D40104100620 | Wet pipe sprinkler systems, steel, light hazard, 1 floor, 10,000 SF | 13600 |  | 3.05 | 48822.91 | 4
D4020 | Standpipes |  |  | 1 | 16036.4 | 3
D40203101540 | Wet standpipe risers, class III, steel, black, sch 40, 4" diam pipe, 1 floor | 1.21 |  | 1 | 16036.4 | 4
D5010 | Electrical Service/Distribution |  |  | 4.87 | 77903.05 | 3
D50101200480 | Overhead service installation, includes breakers, metering, 20' conduit & wire, 3 phase, 4 wire, 120/208 V, 1200 A | 0.89 |  | 1.45 | 23140.53 | 4
D50102300480 | Feeder installation 600 V, including RGS conduit and XHHW wire, 1200 A | 71.11 |  | 1.68 | 26882.35 | 4
D50102400320 | Switchgear installation, incl switchboard, panels & circuit breaker, 120/208 V, 3 phase, 1200 A | 0.85 |  | 1.74 | 27880.17 | 4
D5020 | Lighting and Branch Wiring |  |  | 18.36 | 293706.36 | 3
D50201100640 | Receptacles incl plate, box, conduit, wire, 16.5 per 1000 SF, 2.0 W per SF, with transformer | 12000 |  | 3.64 | 58197.36 | 4
D50201150240 | Receptacle systems, underfloor duct, 5' on center, high density | 4000 |  | 3.06 | 48896.2 | 4
D50201300280 | Wall switches, 2.0 per 1000 SF | 16000 |  | 0.45 | 7215.04 | 4
D50201350320 | Miscellaneous power, 1.2 watts | 16000 |  | 0.33 | 5275.36 | 4
D50201400360 | Central air conditioning power, 8 watts | 16000 |  | 1.13 | 18118.88 | 4
D50201452040 | Motor installation, three phase, 460 V, 10 HP motor size | 5.69 |  | 0.85 | 13614.22 | 4
D50201452080 | Motor installation, three phase, 460 V, 15 HP motor size | 1.42 |  | 0.23 | 3683.52 | 4
D50201452160 | Motor installation, three phase, 460 V, 25 HP motor size | 1.42 |  | 0.27 | 4337.85 | 4
D50201780100 | Variable frequency drive's for 22500 SF computer center | 0.85 |  | 0.97 | 15440.45 | 4
D50202100520 | Fluorescent fixtures recess mounted in ceiling, 1.6 watt per SF, 40 FC, 10 fixtures @32watt per 1000 SF | 18400 |  | 7.43 | 118927.48 | 4
D5030 | Communications and Security |  |  | 32.87 | 525933.76 | 3
D50303100680 | Telephone systems, conduit system with floor boxes, high density | 16000 |  | 6.24 | 99769.28 | 4
D50309100240 | Communication and alarm systems, includes outlets, boxes, conduit and wire, sound systems, 30 outlets | 0.71 |  | 1.85 | 29643.24 | 4
D50309100454 | Communication and alarm systems, fire detection, addressable, 50 detectors, includes outlets, boxes, conduit and wire | 0.85 |  | 2.17 | 34789.12 | 4
D50309100462 | Fire alarm command center, addressable with voice, excl.wire & conduit | 0.71 |  | 0.64 | 10165.72 | 4
D50309200110 | Internet wiring, 8 data/voice outlets per 1000 S.F. | 160 |  | 21.97 | 351566.4 | 4
D5090 | Other Electrical Systems |  |  | 11.7 | 187230.79 | 3
D50902100960 | Generator sets, w/battery, charger, muffler and transfer switch, diesel engine with fuel tank, 350 kW | 497.78 |  | 6.83 | 109354.31 | 4
D50902200310 | Uninterruptible power supply with 15 minutes pack, 375 kVA, 120 V | 0.71 |  | 4.65 | 74376.5 | 4
D50902300300 | Automatic transfer switch, enclosed 120/240 volt, UPS 375 KVA | 0.71 |  | 0.22 | 3499.98 | 4
E | Equipment & Furnishings |  | 0 | 0 | 0 | 1
E1090 | Other Equipment |  |  | 0 | 0 | 3
F | Special Construction |  | 2.62 | 7.82 | 125133.26 | 1
F1020 | Integrated Construction |  |  | 7.82 | 125133.26 | 3
F10201200220 | Special construction, pedestal access floor pkg., inc. stl. pnls, peds. & stringers, 1500 lbs., w/vinyl cov. | 2400 |  | 7.82 | 125133.26 | 4
G | Building Sitework |  | 0 | 0 | 0 | 1
SubTotal |  |  | 100% | $298.26 | 4772155.1
Contractor Fees (General Conditions,Overhead,Profit) |  |  | 25.0% | $74.56 | $1,193,038.78
Architectural Fees |  |  | 7.0% | $26.10 | $417,563.57
User Fees |  |  | 0.0% | $0.00 | $0.00
Total Building Cost |  |  |  | $398.92 | $6,382,757.45