## Archibus
| Assessment Item | CSI ID | Includes | Condition Value | CSI Rating Description
A. SUBSTRUCTURE | Standard Foundations | A1010 | Wall and column foundations, foundation walls and grade beams, pile caps, spread footings, mat foundations, structural slabs on grade, excavation and backfill, perimeter insulation, and anchor plates. | New | Foundation is under 1 year old with no visible defects or settlement. No cracking. Preventative maintenance only.
|  | A1010 |  | Routine Maintenance | No visible signs of cracking, settlement, or water intrusion. Minor surface weathering. No structural impact. Preventative maintenance adequate.
|  | A1010 |  | Minor Repair | Small, non-structural cracks (e.g., shrinkage cracks). No movement. No water entry. Cosmetic repairs or sealants recommended.
|  | A1010 |  | Major Repair | Noticeable cracking or foundation settlement affecting interior finishes. Minor water penetration. Engineering review recommended.
|  | A1010 |  | Replacement | Severe cracking, heaving, sinking, or movement. Structural failure evident. Immediate shoring or reconstruction needed.
| Slab on Grade | A1030 | Structural slabs on grade, thickened slabs, depressed or inclined slabs, slabs with integral trenches or pits, under-slab drainage systems, and under-slab insulation. | New | Slab is newly poured (<1 year), no cracks, no settlement, perfect finish. Preventative maintenance only.
|  | A1030 |  | Routine Maintenance | Surface wear evident, but no cracks or movement. Expansion joints intact. No water intrusion. Cleaning and sealing adequate.
|  | A1030 |  | Minor Repair | Minor cracking (non-structural, shrinkage or surface map cracking). No functional issues. Patching or crack injection recommended.
|  | A1030 |  | Major Repair | Cracking with curling, settlement, or joint damage affecting use. Evidence of water intrusion or base failure. Engineering assessment needed.
|  | A1030 |  | Replacement | Major structural failure: heaving, widespread cracking, subsidence, or slab separation. Full demolition and replacement required.
| Basement Walls | A2020 | Structural basement walls and crawlspace walls, including waterproofing, damp-proofing, thermal insulation, and associated excavation and backfill. | New | Recently constructed walls with effective moisture barrier and no visible defects. No water intrusion. Preventative maintenance only.
|  | A2020 |  | Routine Maintenance | Walls are structurally sound. Moisture barrier intact. Slight efflorescence or discoloration. No visible cracks. Regular inspection sufficient.
|  | A2020 |  | Minor Repair | Hairline cracks, minor signs of moisture seepage (e.g., dampness or surface mold), localized insulation damage. Patch and monitor.
|  | A2020 |  | Major Repair | Visible cracking or bowing. Water penetration during storms. Moisture barrier failing. Structural concern. Repair or reinforce as needed.
|  | A2020 |  | Replacement | Severe structural failure (buckling, collapsing) or chronic water intrusion. Wall replacement and complete remediation necessary.
B. SHELL | Floor Construction | B1010 | Floor structural frame and deck, elevated floor slabs, balconies, mezzanines, inclined and stepped structural floors, suspended ramps, and expansion joints integral to floor systems. Includes catwalks or structural platforms related to floors. | New | Floor structure installed within the past year. No cracks, deflection, or vibration. No corrective action required.
|  | B1010 |  | Routine Maintenance | Structural system intact. No spalling or cracking. Slight wear at joints or edges. Routine inspection and sealant maintenance recommended.
|  | B1010 |  | Minor Repair | Minor cracking or joint separation. No structural movement, but isolated deterioration (e.g., efflorescence, hairline cracks). Repair locally.
|  | B1010 |  | Major Repair | Deflection, vibration, or cracking affecting use. Delamination or corrosion of reinforcing elements. Engineering analysis and reinforcement needed.
|  | B1010 |  | Replacement | Severe degradation or unsafe conditions (e.g., sagging beams, concrete failure, unsafe balconies). Full removal and structural replacement required.
| Roof Construction | B1020 | Roof structural frame and decking, structural roof slabs, sheathing, integrated canopies, and other structural roof systems. Includes structural supports necessary to carry the roof load. | New | Roof framing and deck installed within the past year. No visible defects, corrosion, or deformation. Preventative inspection only.
|  | B1020 |  | Routine Maintenance | Roof structure in good condition. No sagging or separation. Fasteners intact. Minor surface wear or discoloration acceptable.
|  | B1020 |  | Minor Repair | Early signs of corrosion, loose fasteners, or deck deflection. No active leakage. Spot repair of joints or reinforcement needed.
|  | B1020 |  | Major Repair | Sagging beams, corroded steel, delaminated sheathing, or deck failures. Water staining present. Structural reinforcement or partial replacement required.
|  | B1020 |  | Replacement | Structural failure, including collapsed framing or unsafe conditions. Load-bearing capacity compromised. Full replacement of affected areas needed.
| Exterior Walls | B2010 | Exterior wall construction including framing, sheathing, backup walls, insulation, vapor retarders, applied finishes, parapets, louvers, screens, sun control devices, balcony enclosures, railings, and soffits. | New | Exterior wall assembly completed within 1 year. No visible damage, staining, or sealant failure. No repairs needed.
|  | B2010 |  | Routine Maintenance | Wall systems intact with minor fading or dirt. No cracks, gaps, or signs of water intrusion. Regular maintenance like caulking or cleaning recommended.
|  | B2010 |  | Minor Repair | Cracks in finish, loose trim, or localized water stains. Sealant deterioration. Limited corrosion of fasteners. Spot repairs or resealing needed.
|  | B2010 |  | Major Repair | Spalling, water infiltration, degraded vapor barrier, or cladding detachment. Thermal insulation failure. Requires significant repair and component replacement.
|  | B2010 |  | Replacement | Structural damage to wall framing or extensive cladding failure. Repeated moisture intrusion or insulation collapse. Full wall system replacement necessary.
| Exterior Windows | B2020 | Exterior windows, curtain walls, storefront glazing systems, integral coatings or finishes, and wall opening components such as lintels, sills, and flashing. | New | Windows installed within 1 year. No leaks, seal failure, corrosion, or operational issues. Finishes intact. Preventative maintenance only.
|  | B2020 |  | Routine Maintenance | Fully functional. No fogging, sticking, or air/water infiltration. Minor paint or caulk touch-up may be needed.
|  | B2020 |  | Minor Repair | Minor sealant failure, paint flaking, or slight air leaks. Cracked glazing or chipped frames that don’t affect operation. Localized repair needed.
|  | B2020 |  | Major Repair | Multiple failed seals, fogging, hardware malfunctions, air/water infiltration. Warped frames or broken locks. Consider replacing affected units.
|  | B2020 |  | Replacement | Systemic failure: rotted frames, failed curtain wall seals, widespread condensation or leaks. Full window or curtain wall system replacement required.
| Exterior Doors | B2030 | Exterior personnel doors, revolving doors, overhead and sliding doors, hangar and blast-resistant doors, and associated glazing, hardware, and weatherproofing systems. | New | Installed within 1 year. Smooth operation, no damage, fully sealed, and no corrosion. Preventative maintenance only.
|  | B2030 |  | Routine Maintenance | Functional with minor wear. Hardware, glazing, and seals intact. Occasional lubrication or re-caulking may be needed.
|  | B2030 |  | Minor Repair | Minor dents, seal gaps, hardware issues, or paint degradation. No compromise of security or weather resistance. Repair or adjust locally.
|  | B2030 |  | Major Repair | Doors stick, don’t close fully, rust, or have compromised security/weather seals. Replace hardware or door panels as needed.
|  | B2030 |  | Replacement | Doors are warped, heavily corroded, or non-functional. Systemic failure of locking or sealing. Full door system replacement required.
| Roof Coverings | B3010 | Roofing membranes, built-up roofing, shingles or metal systems, traffic coatings (where applicable), vapor retarders, insulation, roof fill, expansion joints, flashings, trim, gutters, downspouts, and eaves/soffits associated with the roofing system. | New | Roofing installed within past year. No ponding, membrane distortion, or sealant issues. Warranty active. Routine inspection only.
|  | B3010 |  | Routine Maintenance | Surface in good condition. Minor granule loss, weathering, or joint shrinkage. Flashings and gutters intact. Caulking or coating touch-ups may be needed.
|  | B3010 |  | Minor Repair | Membrane blistering, flashing separation, isolated ponding, or clogged downspouts. Local patching or sealing recommended.
|  | B3010 |  | Major Repair | Widespread membrane cracking, failed seams, water intrusion evidence. Flashings deteriorated. Partial replacement or significant restoration needed.
|  | B3010 |  | Replacement | Roof system is beyond life expectancy. Leaks present, insulation saturated, or structure at risk. Full tear-off and replacement required.
| Roof Openings | B3020 | Skylights, area glazing systems, roof hatches, gravity ventilators, and smoke vents. Includes flashing, curbs, and waterproofing associated with roof penetrations. | New | Installed within 1 year. No cracks, leaks, or weathering. Operates properly (if operable). Flashing and seals are intact.
|  | B3020 |  | Routine Maintenance | Minor dust or discoloration. No water intrusion. Flashings and gaskets in good condition. Routine cleaning or resealing may be needed.
|  | B3020 |  | Minor Repair | Minor sealant failure, glazing scratches, or surface cracks. Local condensation or small leaks. Repair or reseal locally.
|  | B3020 |  | Major Repair | Glazing is fogged, seals cracked, or leaks recurring. Hatch hardware malfunctioning. Replace affected units or major resealing required.
|  | B3020 |  | Replacement | Systemic failure: major leaks, cracked glazing, non-functional hatches or vents. Full removal and replacement of affected openings required.
C10. INTERIOR CONSTRUCTION | Partitions | C1010 | Fixed and operable partitions, demountable and movable wall systems, interior glazing and storefronts, interior security screens, and integrated railing or screen systems. | New | Recently installed. No visible damage, clean finishes, fully functional operable elements. No adjustments needed.
|  | C1010 |  | Routine Maintenance | Minor wear, no damage. Joints and finishes intact. Operable partitions function properly. Cleaning or minor touch-ups may be needed.
|  | C1010 |  | Minor Repair | Surface damage, minor dents or scuffs, or track issues with operable partitions. Local repairs or adjustments required.
|  | C1010 |  | Major Repair | Partition instability, broken glazing, operable wall failure, or damaged framing. Major repairs or panel replacements needed.
|  | C1010 |  | Replacement | System-wide failure, warped panels, severe damage, or no longer meets function or layout needs. Full replacement necessary.
| Interior Doors | C1020 | Swinging, sliding, folding, glazed, and fire-rated interior doors; hatches and access doors; associated frames, hardware, thresholds, and finishes including painting and staining. | New | Doors and hardware recently installed. Operate smoothly with no signs of wear or damage. No adjustments needed.
|  | C1020 |  | Routine Maintenance | Light wear to finish or hardware. Fully functional with occasional tightening or refinishing recommended.
|  | C1020 |  | Minor Repair | Localized damage (scratches, dents, loose hinges). Minor hardware or finish issues. Repainting or part replacement may be needed.
|  | C1020 |  | Major Repair | Warped doors, hardware failure, misaligned frames, or security/fire code concerns. Multiple replacements or repairs needed.
|  | C1020 |  | Replacement | Systemic failure of door operation, appearance, or code compliance. Widespread damage or degradation. Full replacement necessary.
| Fittings | C1030 | Chalkboards, tackboards, signage and identifying devices, lockers, toilet and bath accessories, storage shelving, handrails and ornamental metals, toilet partitions, cubicles, and closet hardware or specialties. | New | Fittings recently installed. No damage, all functional, finishes intact. No repairs needed.
|  | C1030 |  | Routine Maintenance | Functional with slight wear (e.g., small scratches, fading signage). Cleaning or touch-up may be required.
|  | C1030 |  | Minor Repair | Loose accessories, damaged shelving, scratched surfaces, or malfunctioning toilet accessories. Local repairs needed.
|  | C1030 |  | Major Repair | Damaged or corroded partitions, broken locks or fittings, rusted shelving, or widespread signage issues. Several systems need attention.
|  | C1030 |  | Replacement | Worn, vandalized, missing, or obsolete fittings throughout facility. Systemic failure requiring full replacement of units.
C20. STAIRS | Stair Construction | C2010 | Structural stair framing, treads, risers, landings, and integral handrails or balustrades for interior stair systems. | New | Stair system recently constructed. No wear, movement, or finish defects. Railings are firm and compliant. No maintenance needed.
|  | C2010 |  | Routine Maintenance | Minor scuffing or finish wear. No loose railings or movement. All safety codes met. Cleaning or protective coating touch-up may be recommended.
|  | C2010 |  | Minor Repair | Loose or squeaky treads, minor surface cracks, or worn nosings. Local repair or reinforcement needed.
|  | C2010 |  | Major Repair | Structural movement, rusting components, worn or unsafe treads, loose handrails. Engineering evaluation and partial replacement required.
|  | C2010 |  | Replacement | Stair system unsafe or structurally unsound. Code non-compliance, failing supports, or multiple deteriorated components. Full replacement required.
| Stair Finishes | C2020 | Applied finishes to stair treads, risers, landings, soffits, and to handrails and balustrades. Includes coatings, coverings, and surface treatments. | New | Finishes recently installed. Surfaces are uniform, slip-resistant, and aesthetically consistent. No visible damage or fading.
|  | C2020 |  | Routine Maintenance | Minor wear from foot traffic. Slight scuffing, fading, or polish loss. Cleaning or touch-up refinishing recommended.
|  | C2020 |  | Minor Repair | Localized damage (chips, peeling coatings, cracked tile, etc.). Repairable without full resurfacing.
|  | C2020 |  | Major Repair | Worn, slippery, or damaged finishes that create a hazard. Widespread delamination, loose tiles, or coatings failure. Resurfacing needed.
|  | C2020 |  | Replacement | Systemic failure of finish layer — unsafe conditions or severe aesthetic deterioration. Complete removal and replacement of finishes needed.
C30. INTERIOR FINISHES | Wall Finishes | C3010 | Applied finishes to interior walls, including plaster, wallboard, tile, terrazzo, paint, wallcoverings, acoustic treatments, and other specialty coatings or surface finishes. | New | Finishes recently applied. Clean, uniform appearance. No cracking, peeling, staining, or surface irregularities.
|  | C3010 |  | Routine Maintenance | Minor wear, small scuffs, or fading. No damage or discoloration. Regular cleaning or touch-up painting recommended.
|  | C3010 |  | Minor Repair | Local cracking, peeling, or damaged tile/wallcovering. Limited moisture damage. Repairable without full wall refinishing.
|  | C3010 |  | Major Repair | Widespread finish failure: extensive cracking, peeling paint, or damaged coverings. Likely due to moisture or substrate issues.
|  | C3010 |  | Replacement | Systemic failure of finish layer. Irreparable wall damage, mold, or adhesion failure. Full removal and replacement of wall finishes needed.
| Floor Finishes | C3020 | Applied floor finishes including tile, terrazzo, wood, resilient flooring, carpeting, masonry and stone, floor coatings and sealers, traffic membranes, conductive or specialty flooring, and raised access (pedestal) floor systems. | New | Finishes installed within the past year. Clean, level, and in excellent condition with no signs of wear.
|  | C3020 |  | Routine Maintenance | Minor wear or discoloration in high-traffic areas. No loose tiles or peeling surfaces. Cleaning, buffing, or resealing may be needed.
|  | C3020 |  | Minor Repair | Scuffed or scratched surfaces, small areas of adhesive failure, carpet fraying, or tile damage. Localized repair or patching needed.
|  | C3020 |  | Major Repair | Widespread surface failure — curled edges, cracking, seam separation, or water-damaged carpet. Requires section replacement or refinishing.
|  | C3020 |  | Replacement | Flooring is beyond repair — safety hazard due to tripping, contamination, or delamination. Entire flooring system requires replacement.
| Ceiling Finishes | C3030 | Suspended and applied ceiling finishes including acoustic tiles and panels, plaster, wallboard, painted or stained surfaces, exposed concrete, metal ceilings, and specialty ceiling types. | New | Ceiling finishes installed within the past year. Uniform appearance, no cracks, warping, or staining. No maintenance required.
|  | C3030 |  | Routine Maintenance | Minor discoloration or dust buildup. No loose panels or flaking paint. Cleaning or repainting recommended.
|  | C3030 |  | Minor Repair | Localized damage such as stained tiles, peeling paint, or cracked plaster. Replace or patch in limited areas.
|  | C3030 |  | Major Repair | Widespread sagging, staining from roof leaks, damaged grid systems, or safety issues. Full ceiling grid or finish repair recommended.
|  | C3030 |  | Replacement | Ceiling system is beyond useful life. Extensive damage or outdated material requires complete system removal and replacement.
D10. CONVEYING SYSTEMS | Elevators & Lifts | D1010 | Passenger elevators, freight elevators, wheelchair and platform lifts, and other vertical transportation systems. | New | Newly installed. Quiet, smooth operation, fully compliant with accessibility and safety standards. No repairs or adjustments needed.
|  | D1010 |  | Routine Maintenance | Normal operation. Minor wear to doors or controls. Maintenance log up to date. Preventative maintenance such as lubrication or inspection may be required.
|  | D1010 |  | Minor Repair | Occasional minor malfunctions, delayed door operations, or worn buttons. Does not impact safety. Minor part replacements or service call needed.
|  | D1010 |  | Major Repair | Frequent breakdowns, failed sensors, outdated controls, or non-compliant safety features. Requires significant component replacement or upgrades.
|  | D1010 |  | Replacement | Non-functional system or fails inspection. Obsolete components or inaccessible for users with disabilities. Full system replacement necessary.
D20. PLUMBING | Plumbing Fixtures | D2010 | Water closets, urinals, lavatories, sinks, showers, bathtubs, drinking fountains, bidets, and associated trim and control components. | New | Recently installed fixtures. No leaks, corrosion, or damage. ADA-compliant. No action needed.
|  | D2010 |  | Routine Maintenance | Fully functional. Minor wear such as loose handles or dull finishes. Cleaning, lubrication, or minor tightening may be needed.
|  | D2010 |  | Minor Repair | Dripping faucets, cracked porcelain, or clogged drains. No water damage. Localized repairs or fixture parts replacement recommended.
|  | D2010 |  | Major Repair | Leaking seals, broken handles, damaged enclosures or inaccessible units. Multiple repairs or fixture replacement required.
|  | D2010 |  | Replacement | Systemic failure: non-functional, rusted, non-code-compliant, or extensively damaged. Full replacement of fixture(s) necessary.
| Domestic Water Distribution | D2020 | Interior domestic water distribution systems including piping, fittings, valves, hose bibbs, water heaters, pressure tanks, domestic water equipment, and pipe insulation. | New | Recently installed piping and equipment. No corrosion, leaks, or performance issues. Meets code and energy standards.
|  | D2020 |  | Routine Maintenance | Operational with minor surface oxidation or valve wear. Water heater functional. Periodic flushing or valve replacement may be needed.
|  | D2020 |  | Minor Repair | Drips at fittings, valve leaks, degraded insulation, or underperforming water heaters. Repairs or spot insulation replacement required.
|  | D2020 |  | Major Repair | Frequent leaks, deteriorated piping, rusted fittings, or malfunctioning heaters. Large portions of system need repair or equipment replacement.
|  | D2020 |  | Replacement | System failure or end-of-life components (e.g., galvanized steel pipe failure, tank rupture). Full system or major section replacement required.
| Sanitary Waste | D2030 | Sanitary waste and vent piping systems, including pipe fittings, floor drains, cleanouts, associated equipment (e.g., sump pumps, grease traps), and pipe insulation. | New | System recently installed. No leaks, odors, corrosion, or venting issues. Equipment operates as designed.
|  | D2030 |  | Routine Maintenance | System is functional. Minor signs of buildup or aging. No leaks. Periodic inspection or cleaning of traps or vents may be needed.
|  | D2030 |  | Minor Repair | Localized corrosion, cracked cleanout caps, or partial blockages. Drains may need clearing. Small section repairs or equipment servicing required.
|  | D2030 |  | Major Repair | Recurring backups, pipe corrosion, deteriorated venting, or failed pumps. Multiple repairs or partial replacements required.
|  | D2030 |  | Replacement | Extensive pipe deterioration, chronic failure, or outdated materials (e.g., cast iron failure). Full system or large-scale replacement required.
| Rain Water Drainage | D2040 | Interior rainwater drainage piping systems, including roof drains, pipe and fittings, and associated insulation. Excludes gutters and downspouts (see B3010 – Roof Coverings). | New | System recently installed. No leaks, corrosion, clogs, or water ponding. All drains and piping are clear and well insulated.
|  | D2040 |  | Routine Maintenance | Fully functional system. Minor buildup or discoloration around drains. No active leaks. Routine inspection and occasional clearing recommended.
|  | D2040 |  | Minor Repair | Leaking fittings, clogged drains, or insulation deterioration. Localized repairs and drain clearing needed.
|  | D2040 |  | Major Repair | Frequent backups, corroded piping, water infiltration through roof drains. Partial pipe or drain system replacement may be needed.
|  | D2040 |  | Replacement | Systemic failure — extensive rust, leaks, or undersized drains leading to water intrusion. Full system or major section replacement required.
| Pool Systems | D2050 | Includes mechanical, plumbing, and treatment systems for pools, spas, and aquatic features. Covers filtration, circulation, water chemistry systems, pool heaters, pumps, and piping necessary to operate and maintain aquatic environments. | New | Recently installed pool system. Fully functional and code compliant.
|  | D2050 |  | Routine Maintenance | Systems in good condition. Routine service needed (e.g., filter changes, chemical balancing).
|  | D2050 |  | Minor Repair | Minor leaks, clogged filters, or sensor issues. Correctable without affecting pool operation.
|  | D2050 |  | Major Repair | Pump or heater failure, corroded piping, or persistent chemistry/control faults. Pool use may be disrupted.
|  | D2050 |  | Replacement | System beyond life expectancy or with repeated failures. Unsafe or inoperable. Full replacement of major equipment or piping needed.
D30. HVAC | Energy Supply | D3010 | Energy supply systems including fossil fuels (oil, gas, coal), central plant steam, hot water, and chilled water, and on-site renewable sources such as solar and wind energy. | New | Recently installed energy supply connections and systems. Operating efficiently with no visible wear or performance issues.
|  | D3010 |  | Routine Maintenance | Fully operational. No leaks or pressure drops. Minor calibration, inspection, or system balancing may be needed.
|  | D3010 |  | Minor Repair | Leaks at joints, corroded pipes, or sensors malfunctioning. Repairs localized and do not impact overall service continuity.
|  | D3010 |  | Major Repair | Pressure failures, corroded main lines, non-functioning renewable components (e.g., inverter faults). Partial system shutdowns or losses.
|  | D3010 |  | Replacement | Aging or obsolete supply systems (e.g., rusted oil lines, failed solar arrays). Full replacement of system or transition to alternative energy required.
| Heat Generating Systems | D3020 | Boilers (including electric), primary heating pumps, adjacent piping and fittings, auxiliary heating components (e.g., burners, heat exchangers), and associated insulation. | New | Recently installed system. Fully functional and efficient. No corrosion, leaks, or calibration issues.
|  | D3020 |  | Routine Maintenance | Operating within design parameters. Regular servicing required (e.g., cleaning burners, inspecting controls). Minor wear on insulation or components.
|  | D3020 |  | Minor Repair | Leaking pump seals, control malfunctions, localized corrosion, or insulation deterioration. Minor repairs and recalibration needed.
|  | D3020 |  | Major Repair | Boiler inefficiency, major corrosion, scale buildup, or repeated component failure. Burner or pump replacements may be required.
|  | D3020 |  | Replacement | Boiler beyond useful life, unsafe to operate, or parts no longer supported. Full replacement of heat generation system needed.
| Cooling Generating Systems | D3030 | Chillers, direct expansion (DX) systems, cooling towers, evaporative coolers, condensers, primary cooling pumps, and associated piping, fittings, and insulation. Also includes condensing units for split and rooftop systems. | New | Recently installed. Cooling systems operate efficiently with no signs of wear, leaks, or control issues. Preventative maintenance only.
|  | D3030 |  | Routine Maintenance | Fully functional. Minor vibration, surface corrosion, or insulation wear. Seasonal maintenance and filter changes may be needed.
|  | D3030 |  | Minor Repair | Leaks in piping, coil fouling, pump noise, or refrigerant loss. Repairs or component replacement needed but system still functional.
|  | D3030 |  | Major Repair | Chiller inefficiency, failing compressor, tower deterioration, or repeated failures. Partial replacement or major servicing needed.
|  | D3030 |  | Replacement | Equipment near or beyond life expectancy, non-functional, or obsolete. Full system replacement or upgrade required.
| Distribution Systems | D3040 | Air and hydronic distribution systems including AHUs, ductwork, VAV boxes, terminal units, exhaust systems, heat exchangers, secondary pumps, sound attenuation, and insulation for piping and ductwork. Covers supply/return air, ventilation, and steam, hot/chilled water, and glycol systems. Excludes water and steam unit heaters. | New | Distribution systems recently installed. All ductwork and piping is clean, sealed, insulated, and operating efficiently.
|  | D3040 |  | Routine Maintenance | Minor dust buildup, slight insulation wear, or filter replacement needed. Terminal units function properly. System balancing or cleaning may be required.
|  | D3040 |  | Minor Repair | Isolated air leaks, stuck dampers, failing actuators, or slight corrosion on hydronic piping. Localized repair or re-insulation recommended.
|  | D3040 |  | Major Repair | Widespread duct leakage, corroded piping, failing coils or terminal units, or imbalanced airflow. Requires significant partial system repair.
|  | D3040 |  | Replacement | System is outdated, corroded, or non-functional. Major components failing. Full replacement of air or water distribution system needed.
| Controls & Instrumentation | D3060 | Central and local HVAC controls, including thermostats, sensors, actuators, control valves, timers, and building automation systems (BAS). Includes instrumentation for temperature, pressure, and flow, and all control wiring, interfaces, and network cabling associated with HVAC system regulation and energy management. | New | Modern, fully operational controls and instrumentation. Connected to BAS or programmable systems. Responsive and efficient.
|  | D3060 |  | Routine Maintenance | Functional but may require software updates, calibration, or occasional replacement of thermostats or sensors. System tuning recommended.
|  | D3060 |  | Minor Repair | Non-responsive zones, sensor drift, or actuator failure in localized areas. Repairs or recalibration needed to restore full function.
|  | D3060 |  | Major Repair | Multiple zones affected, failed controllers, or outdated software. BAS interface unreliable. Major repairs or system reprogramming required.
|  | D3060 |  | Replacement | Controls are obsolete, non-functional, or incompatible with HVAC equipment. Full system replacement with modern DDC/BAS recommended.
D40. FIRE PROTECTION | Sprinklers | D4010 | Automatic fire sprinkler systems including water supply equipment, piping, valves, fittings, sprinkler heads, and release devices. Includes wet, dry, or pre-action systems and their connection to building water or fire mains. | New | Recently installed. Fully functional and code-compliant. All components tested and certified.
|  | D4010 |  | Routine Maintenance | Functional with no leaks. Minor corrosion or dust buildup. Periodic testing, flushing, or inspection required.
|  | D4010 |  | Minor Repair | Dripping fittings, partially blocked heads, or inoperative zones. Repairs localized and not affecting full coverage.
|  | D4010 |  | Major Repair | Failing heads, inoperative valves, or corroded piping. Significant repairs or replacement of zones or supply piping needed.
|  | D4010 |  | Replacement | System non-functional, obsolete, or out of compliance with current codes. Full replacement of sprinkler system or conversion to compliant type.
| Standpipes | D4020 | Standpipe systems including risers, piping, control valves, hose connections, hose cabinets, and water supply equipment. Includes wet, dry, or combination systems used for fire protection, excluding automatic sprinklers (see D4010). | New | System recently installed and fully compliant. No corrosion, blockages, or leaks. All components certified.
|  | D4020 |  | Routine Maintenance | Minor corrosion, dust, or aging of non-critical components. Cabinet doors or hoses may need cleaning or lubrication. Regular inspection sufficient.
|  | D4020 |  | Minor Repair | Leaking joints, missing caps, or hose wear. Repairs needed to isolated components, no loss of system function.
|  | D4020 |  | Major Repair | Corrosion, valve seizure, or pressure issues affecting one or more zones. Section replacement or valve refurbishment required.
|  | D4020 |  | Replacement | Widespread failure, non-compliance with current fire code, or obsolete components. Full system or zone replacement necessary.
| Fire Protection Specialties | D4030 | Portable fire extinguishers and associated wall-mounted or recessed cabinets. Includes standalone fire protection accessories not integrated with sprinkler or standpipe systems. | New | Extinguishers and cabinets recently installed. Fully charged, labeled, accessible, and compliant.
|  | D4030 |  | Routine Maintenance | Fully functional. May require recharge, inspection tag update, or cleaning. No damage or obstruction.
|  | D4030 |  | Minor Repair | Faded labels, loose brackets, or surface rust on cabinet. Still functional. Minor repairs or replacement of parts needed.
|  | D4030 |  | Major Repair | Expired extinguishers, broken cabinets, missing hardware, or inaccessible locations. Multiple units require replacement or relocation.
|  | D4030 |  | Replacement | Units missing, discharged, corroded, or beyond useful life. Full replacement of extinguishers and/or cabinets required for compliance.
D50. ELECTRICAL | Electrical Service & Distribution | D5010 | Electrical service entrance equipment including primary and secondary transformers, main switchboard, panelboards, enclosed breakers, motor control centers, and conduit with wiring for building distribution systems. | New | Recently installed system. All components clean, labeled, fully operational, and compliant with electrical code.
|  | D5010 |  | Routine Maintenance | No issues, minor dust buildup. Periodic thermal scanning, torque checks, and cleaning required.
|  | D5010 |  | Minor Repair | Isolated breaker trips, worn labels, or minor corrosion. Replacement of breakers or bus bar insulation may be needed.
|  | D5010 |  | Major Repair | Obsolete switchgear, persistent faults, damaged MCCs, or deteriorated wiring. Requires panel or MCC replacement.
|  | D5010 |  | Replacement | System beyond useful life, non-compliant, or unsafe. Full replacement of distribution equipment and associated conduit required.
| Lighting & Branch Wiring | D5020 | Branch wiring and devices for lighting and equipment connections, including interior and exterior lighting fixtures, switches, sensors, and receptacles. Covers branch wiring to non-mechanical devices and exterior building-mounted lighting. | New | Recently installed. All lighting fixtures and devices are operational, energy-efficient, and compliant. No defects or discoloration.
|  | D5020 |  | Routine Maintenance | Minor lamp or driver failures. Some fixture cleaning or relamping required. Wiring and devices in good condition.
|  | D5020 |  | Minor Repair | Flickering lights, loose devices, or aging switches. Localized wiring or fixture repairs recommended.
|  | D5020 |  | Major Repair | Frequent outages, wiring deterioration, broken fixtures, or non-compliant components. Replacement of major fixture groups or wiring needed.
|  | D5020 |  | Replacement | System obsolete, non-functional, or unsafe. Requires full lighting and branch wiring replacement throughout the building.
| Communications & Security | D5030 | Communications and security systems including fire alarms, telephones, data networks, intercoms, public address, paging, clock systems, call systems, TV, and security components such as access control and video surveillance. | New | Recently installed systems. Fully functional and code-compliant. All devices connected and operational.
|  | D5030 |  | Routine Maintenance | Systems operational. May require software updates, battery replacements, or testing. Occasional device recalibration or cleaning may be needed.
|  | D5030 |  | Minor Repair | Intermittent device failure (e.g., phone, camera, sensor), damaged wires, or minor communication issues. Component-level repair needed.
|  | D5030 |  | Major Repair | System-wide outages, fire alarm faults, or non-functioning security zones. Multiple device or controller replacements required.
|  | D5030 |  | Replacement | Obsolete or unsupported system, non-code-compliant, or critical failure. Full replacement of fire alarm, security, or communication system needed.
| Other Electrical Systems | D5090 | Auxiliary electrical systems including emergency generators, UPS, emergency lighting, lightning protection, grounding, power factor correction, raceway systems, and on-site power generation systems such as solar or cogeneration units. | New | All components recently installed and tested. Fully operational with code compliance.
|  | D5090 |  | Routine Maintenance | Operational with no faults. Minor wear, battery testing, or scheduled maintenance (e.g., load testing for generators) may be required.
|  | D5090 |  | Minor Repair | Limited failures such as damaged conduits, worn grounding lugs, or UPS alerts. Repairs localized and do not affect system reliability.
|  | D5090 |  | Major Repair | Generator or UPS performance issues, lightning protection failures, or faulty grounding. Requires significant repair or component replacement.
|  | D5090 |  | Replacement | Obsolete systems, safety risks, or total failure. Full system replacement (e.g., generator, UPS, or raceway system) is needed.
E10. EQUIPMENT | Institutional Equipment | E1020 | Fixed or built-in institutional equipment including items for religious, library, theater, laboratory, classroom, medical, and mortuary use. Includes AV systems and specialty furnishings integral to facility function. | New | Recently installed and operational. Clean, calibrated, and fully functional.
|  | E1020 |  | Routine Maintenance | Equipment fully functional. Minor wear. Scheduled inspection, lubrication, or cleaning may be needed.
|  | E1020 |  | Minor Repair | Surface wear, minor mechanical/electrical failures, or calibration issues. Local repair or part replacement required.
|  | E1020 |  | Major Repair | Repeated equipment failure, loss of accuracy, or functional limitations. Repairs needed across multiple systems or components.
|  | E1020 |  | Replacement | Equipment obsolete, unsafe, or beyond useful life. Full system or category replacement required (e.g., detention furniture, lab hoods, AV systems).
| Vehicular Equipment | E1030 | Equipment for vehicle service, parking control, and loading docks. Includes vehicle lifts, lubrication systems, parking gates and controls, and dock levelers, bumpers, and restraints. | New | Equipment recently installed, fully functional, and code-compliant.
|  | E1030 |  | Routine Maintenance | Minor wear. Functional with regular servicing (e.g., gate sensors, dock bumpers, or lift lubrication).
|  | E1030 |  | Minor Repair | Localized failures such as stuck gate arms, worn seals, or dock leveler damage.
|  | E1030 |  | Major Repair | Multiple inoperable units, hydraulic failure, or structural damage requiring rebuild or extensive servicing.
|  | E1030 |  | Replacement | Systems outdated, unsafe, or non-functional. Full replacement needed for safe vehicle servicing or loading.
| Detention Equipment | E1040.7 | Fixed equipment for detention use, including security doors, locks, glazing, barriers, gates, monitoring devices, and control systems. Designed to maintain secure conditions in correctional or detention facilities. | New | Recently installed equipment, fully secure and code-compliant. No signs of tampering or wear.
|  | E1040.7 |  | Routine Maintenance | Functional with minor cosmetic wear or lubrication needs. Periodic inspection of locks, glazing, or hardware required.
|  | E1040.7 |  | Minor Repair | Sticking doors, loose hardware, or worn finishes. Repairs do not impact immediate security.
|  | E1040.7 |  | Major Repair | Malfunctioning locks, damaged glazing, or non-responsive control panels. Security may be compromised; urgent repair required.
|  | E1040.7 |  | Replacement | Obsolete or failed equipment presenting safety/security risks. Requires full replacement of affected systems or furnishings.
| Other Equipment | E1090 | Miscellaneous equipment including janitorial tools, waste handling, unit kitchens, residential appliances, agricultural devices, and specialized items such as darkroom, athletic, therapeutic, observatory, and planetarium equipment not classified elsewhere in Division E10. | New | Recently installed, fully functional, clean, and code-compliant.
|  | E1090 |  | Routine Maintenance | Equipment operational with minor signs of wear. Periodic servicing (e.g., filter changes, cleaning) required.
|  | E1090 |  | Minor Repair | Minor component damage or malfunctions. Repairs limited to individual parts or control units.
|  | E1090 |  | Major Repair | Frequent failures, loss of function, or non-compliance. Multiple units affected or system-level repair needed.
|  | E1090 |  | Replacement | Equipment is obsolete, unsafe, or fully inoperable. Requires full replacement due to age or performance issues.
E20. FURNISHINGS | Fixed Furnishings | E2010 | Built-in furnishings including fixed casework, artwork, window treatments, recessed floor grilles and mats, fixed seating, and interior landscaping features. Items are permanently affixed and serve functional or decorative roles. | New | Recently installed and in excellent condition. No defects or damage. Fully functional and attractive.
|  | E2010 |  | Routine Maintenance | Good condition overall. Minor wear, scuffing, or cleaning needs. No functional issues.
|  | E2010 |  | Minor Repair | Loose hardware, worn finishes, or minor surface damage. Cosmetic or small repairs needed.
|  | E2010 |  | Major Repair | Structural damage to casework, broken seating, or significant fading/warping. Widespread repairs or replacements needed.
|  | E2010 |  | Replacement | Fixtures are obsolete, damaged beyond repair, or no longer function as intended. Full replacement required.
F10. Special Construction | Integrated Construction | F1020 | Includes modular or prefabricated systems for data centers such as raised access flooring, equipment pods, and integrated utility racks. Supports IT infrastructure with built-in cable pathways, cooling channels, and structural framing for dense equipment environments. | New | Recently installed, fully functional, tight tolerances, all interfaces sealed and aligned.
|  | F1020 |  | Routine Maintenance | Operates as designed; routine checks of panels, airflow paths, and anchoring required.
|  | F1020 |  | Minor Repair | Loose tiles, scuffed surfaces, or non-critical misalignments requiring minor fixes.
|  | F1020 |  | Major Repair | Significant structural or utility path failures impacting cooling, cabling, or access.
|  | F1020 |  | Replacement | System outdated, structurally unsound, or incompatible with modern IT needs; full system replacement required.